## Degradation Calculator
Central Heating & Cooling Degradation Calculator | [8 empty] | Degradation Calculator Instructions |  | Table 1 |  | Table 2 |  |  |  | Table 3
[11 empty] | Type of Heating Equipment | Base AFUE | Type of Air Conditioning or Heat-Pump Equipment | Base SEER | Base EER | Base HSPF | Year of System | Typical SEER
Client Name | [6 empty] | Current Calendar Year |  | Enter the current calendar year at the time of intial assessment. |  | Condensing gas furnace | 90 | Split central air conditioner, two - speed reciprocating compressor, electronically commutated air handler motor (ECM), thermostatic expansion valve (TXV), fan coil | 14 | 10.5 |  | Pre-1980 | 6.5
Job # | [9 empty] | Conditioned space | Gas furnace, direct-vent or forceddraft combustion, electronic ignition, in conditioned space | 80 | Split central air conditioner, single - speed scroll compressor, ECM air handler motor, cased coil | 12 | 10.8 |  | 1980 | 6.5
[10 empty] | Unconditioned space | Gas furnace, natural-draft combustion, vent damper, electronic ignition, in conditioned space | 78 | Split central air conditioner, single - speed reciprocating compressor, PSC air-handler motor, cased coil (after 1991) | 10 | 9.3 |  | 1981 | 8
Degradation of Heating Systems | [6 empty] | Select Furnace Location |  | Enter this information if it can be found on the information plate. |  | Gas furnace, natural-draft combustion, standing pilot light, in conditioned space | 75 | Split central air conditioner, single -speed reciprocating compressor, PSC air-handler motor, cased coil (1981 -1991) | 8 | 7.7 |  | 1982 | 8
Funding Source | [6 empty] | Select Funding Source |  | A. | Select funding source(s) to be used to weatherize the unit | Gas furnace, natural-draft combustion, standing pilot light, no vent damper, in unconditioned space | 64 | Split central air conditioner, single -speed reciprocating compressor, PSC air-handler motor, cased coil (before 1981) | 6.5 | 6.4 |  | 1983 | 8
Furnace Type | [6 empty] | Select Furnace Type |  | B. | Select the type furcentral furnace in the unit to be weatherized. | Gas hot water boiler, natural-draft combustion, standing pilot light | 80 | Split heat pump, single-speed scroll compressor, ECM air handler motor, TXV valve | 14 | 10.5 | 8 | 1984 | 8
Manufactured Year (found on name plate in the serial number) | [8 empty] | c. | Enter the documented Manufactured Year of the existing unit. | Gas steam boiler | 81 | Split heat pump, single-speed reciprocating compressor, PSC air-handler motor (after 1991) | 10 | 9.3 | 7.1 | 1985 | 8
AFUE/Efficiency | [10 empty] | Condensing gas boiler | 90 | Split heat pump, single-speed reciprocating compressor, PSC air-handler motor (1981-1991) | 8 | 7.7 | 6.6 | 1986 | 8
Gas Unit (required from combustion analyzer efficiency reading) | [8 empty] | D. | Enter the AFUE of the existing furnace from combustion analyzer efficiency reading. | Gas hot water / fan-coil combo system | 80 | Split heat pump, single-speed reciprocating compressor, PSC air-handler motor (before 1981) | 6.5 | 6.4 | 6 | 1987 | 8
FALSE | FALSE | FALSE | FALSE | FALSE | FALSE |  | FALSE
Electric Resistance Furnace (Base Efficiency) | [8 empty] | E. | Automated selection based on DOE guidelines | Gas boiler / tankless coil combo system | 80 | Packaged central air conditioner, single-speed reciprocating compressor, PSC air-handler motor | 10 | 9.1 |  | 1988 | 8
Heat Pump (Base HSPF) (If unknown leave blank) | [8 empty] | F. | Automated selection based on DOE guidelines | Gas space heater, fan type | 73 | Packaged heat pump, singlespeed reciprocating compressor, PSC air-handler motor | 10 | 9.1 | 6.8 | 1989 | 8
Equipment Maintenance | [6 empty] | Annual Professional Maintenance |  | G. | Enter the estimated maintenance done on the unit. Choose one of two options. | Gas space heater, gravity type | 60 | Room air conditioner, louvered sides, cooling only, single-speed compressor, PSC fan motor, |  | 9.75 |  | 1990 | 8
Maintenance Factor | [8 empty] | H. | The Maintenance Factor will be automatically determined based on the selections above. | Oil furnace, flame-retention burner, vent dampers, in conditioned space | 81 | Room air conditioner, louvered sides, cooling only, single-speed compressor, PSC fan motor, |  | 8.5 |  | 1991 | 8
Degraded AFUE/Efficiency | [8 empty] | I. | The degraded AFUE will be autocalculated using the info input throughout the form. | Oil furnace, conventional burner, no vent dampers, in conditioned space | 71 | Room air conditioner, louvered sides, cooling only, single-speed compressor, PSC fan motor, (1981-1991) |  | 7.5 |  | 1992 | 10
AFUE = (Base AFUE) * (1-M)^age | [10 empty] | Oil hot water boiler, forced-draft combustion | 80 | Room air conditioner, louvered sides, cooling only, single-speed compressor, PSC fan motor, (before 1981) |  | 6.5 |  | 1993 | 10
Base AFUE = Typical efficiency of Pre-Retrofit equipment when new | [10 empty] | Oil steam boiler | 82 | Room electric heat pump, louvered sides, single-speed compressor, PSC fan motor, < 20,000 Btu/hr |  | 9 |  | 1994 | 10
M = Maintenance Factor | [10 empty] | Electric-resistance furnace or boiler, conditioned space | 100 | Room electric heat pump, louvered sides, single-speed compressor, PSC fan motor, ≥20,000 Btu/hr |  | 8.5 |  | 1995 | 10
Age = Age of equipment in years. | [10 empty] | Electric-resistance furnace or boiler, unconditioned space | 98 | Direct evaporative cooling |  | 25 |  | 1996 | 10
http://www.nrel.gov/docs/fy06osti/38238.pdf | [10 empty] | Electric-resistance baseboard heating | 100 | Source: http://www.nrel.gov/docs/fy06osti/38238.pdf |  |  |  | 1997 | 10
[11 empty] | Electric space heater | [5 empty] | 1998 | 10
Degradation of Central Air Conditioning Systems | [8 empty] | Enter this information if it can be found on the information plate. |  | Source: http://www.nrel.gov/docs/fy06osti/38238.pdf | [5 empty] | 1999 | 10
Funding Source | [6 empty] | Select Funding Source |  | A. | Select funding source(s) to be used to weatherize the unit | [6 empty] | 2000 | 12
Cooling Equipment Type | [6 empty] | Select Cooling Equipment |  | B. | Select the type furcentral furnace in the unit to be weatherized. | [6 empty] | 2001 | 12
Manufactured Year (found on the plate or Building Intelligence Center) | [8 empty] | c. | Enter the documented Manufactured Year of the existing unit. | [6 empty] | 2002 | 12
FALSE | FALSE | FALSE | FALSE | FALSE | FALSE
SEER/EER (found on the plate) (if unknown leave blank) | [8 empty] | B. | Verify auto-population with Table 3 to the right. | [6 empty] | 2003 | 12
Equipment Maintenance | [6 empty] | Seldom or Never Maintained |  | C. | Enter the estimated maintenance done on the unit. Choose one of two options. | [6 empty] | 2004 | 12
Maintenance Factor | [8 empty] | D. | The Maintenance Factor will be automatically determined based on the selections above. | [6 empty] | 2005 | 12
0 | [5 empty] | FALSE | SEER
Degraded SEER/EER | [8 empty] | E. | The degraded SEER/EER will be autocalculated using the info input throughout the form. | [6 empty] | 2006 | 12
EFF = (Base EFF) * (1-M)^age | [6 empty] | http://www.nrel.gov/docs/fy06osti/38238.pdf | [9 empty] | 2007 | 12
Base EFF = Typical efficiency of equipment when new (SEER, EER, or HSPF) | [6 empty] | WPN-23-6 | [9 empty] | 2008 | 12
M = Maintenance Factor | [16 empty] | 2009 | 14
Age = Age of equipment in years. | [7 empty] | Rev.4/3/2024 | [8 empty] | 2010 | 14
[17 empty] | 2011 | 14
[17 empty] | 2012 | 14
[17 empty] | 2013 | 14
[17 empty] | 2014 | 14.5
[17 empty] | 2015 | 14.5
[17 empty] | 2016 | 15
[17 empty] | 2017 | 15
[17 empty] | 2018 | 15
[17 empty] | 2019 | 15
[17 empty] | 2020 | 15
[17 empty] | 2021 | 15
[17 empty] | 2022 | 15
[17 empty] | 2023 | 15.2
[17 empty] | 2024 | 15.2
[17 empty] | 2025 | 15.2
[17 empty] | 2026 | 15.2

## Sheet1 (hidden)
AFUE/Efficiency - Gas Furnace
[8 empty] | H12 | I&J12
0
A13 | B13 | C13 | D13 | E13 | F13 | G13 | H13 |  | J13
FALSE | FALSE | FALSE | FALSE | FALSE | FALSE |  | FALSE